## IRL
Sampling Location, Date:
|  | IRL, 3/21/2013 |  |  |  |  | IRL, 9/25/2015
Sample Components | Unit | Bylaw | Result | RDL | RC Batch | Compliance(Y/N) | Bylaw | Result | RDL | RC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Calculated Parameters
Total Animal/Vegetable Oil and Grease | mg/L | 150 | 13 | 0.5 | 3159223 | Y | 150 | 10 | 0.5 | 4204544 | Y
Inorganics
Total BOD | mg/L | 300 | 280 | 2 | 3159541 | Y | 300 | 360 | 2 | 4206898 | N | Y
Fluoride (F-) | mg/L | 10 | 0.6 | 0.1 | 3160351 | Y | 10 | 0.61 | 0.1 | 4209055 | Y
Total Kjeldahl Nitrogen (TKN) | mg/L | 100 | 93 | 2 | 3167955 | Y | 100 | 120 | 10 | 4210940 | N | Y
pH | pH | 6.0:11.5 | 8.57 |  | 3160350 | Y | 6.0:11.5 | 8.69 | N/A | 4209051 | Y | #VALUE!
Phenols-4AAP | mg/L | 1 | 0.075 | 0.001 | 3220580 | Y | 1 | 0.076 | 0.05 | 4208475 | Y
Total Suspended Solids | mg/L | 350 | 780 | 20 | 3160851 | N | 350 | 79 | 10 | 4210772 | Y
Total Cyanide (CN) | mg/L | 2 | ND | 0.005 | 3161612 |  | 2 | 0.019 | 0.005 | 4212211 | Y
Miscellaneous Parameters
Nonylphenol Ethoxylate (Total) | mg/L | 0.2 | 0.095 | 0.025 | 3161952 | Y | 0.2 | 0.062 | 0.025 | 4209335 | Y
Nonylphenol (Total) | mg/L | 0.02 | 0.005 | 0.001 | 3161948 | Y | 0.02 | 0.003 | 0.001 | 4209322 | Y
Petroleum Hydrocarbons
Total Oil & Grease | mg/L | - | 13 | 0.5 | 3162970 | Y | NV | 10 | 0.5 | 4213097
Total Oil & Grease Mineral/Synthetic | mg/L | 15 | ND | 0.5 | 3162991 |  | 15 | <0.50 | 0.5 | 4213114 | Y
ELEMENTS BY ATOMIC SPECTROSCOPY (WATER)
Metals
Total Aluminum (Al) | mg/L | 50 | ND | 0.1 | 3168265 |  | 50 | 0.7 | 0.1 | 4208707 | Y
Total Antimony (Sb) | mg/L | 5 | ND | 0.2 | 3168265 |  | 5 | <0.02 | 0.02 | 4208707 | Y
Total Arsenic (As) | mg/L | 1 | ND | 0.2 | 3168265 |  | 1 | <0.01 | 0.01 | 4208707 | Y
Total Cadmium (Cd) | mg/L | 0.7 | ND | 0.005 | 3168265 |  | 0.7 | <0.002 | 0.002 | 4208707 | Y
Total Chromium (Cr) | mg/L | 4 | ND | 0.01 | 3168265 |  | 4 | <0.01 | 0.01 | 4208707 | Y
Chromium (VI) | ug/L | 2000 | ND | 0.5 | 3161903 |  | 2000 | <0.50 | 0.5 | 4209685 | Y
Total Cobalt (Co) | mg/L | 5 | ND | 0.02 | 3168265 |  | 5 | <0.002 | 0.002 | 4208707 | Y
Total Copper (Cu) | mg/L | 2 | 0.18 | 0.02 | 3168265 | Y | 2 | 0.21 | 0.01 | 4208707 | Y
Total Lead (Pb) | mg/L | 1 | ND | 0.05 | 3168265 |  | 1 | <0.01 | 0.01 | 4208707 | Y
Total Manganese (Mn) | mg/L | 5 | 0.02 | 0.01 | 3168265 | Y | 5 | 0.053 | 0.001 | 4208707 | Y
Mercury (Hg) | mg/L | 0.01 | ND | 0.0001 | 3167146 |  | 0.01 | <0.00010 | 0.0001 | 4208547 | Y
Total Molybdenum (Mo) | mg/L | 5 | ND | 0.02 | 3168265 |  | 5 | <0.005 | 0.005 | 4208707 | Y
Total Nickel (Ni) | mg/L | 2 | ND | 0.05 | 3168265 |  | 2 | 0.006 | 0.005 | 4208707 | Y
Total Phosphorus (P) | mg/L | 10 | 9.6 | 0.1 | 3168265 | Y | 10 | 8.9 | 0.05 | 4208707 | Y | Y
Total Selenium (Se) | mg/L | 1 | ND | 0.2 | 3168265 |  | 1 | <0.02 | 0.02 | 4208707 | Y
Total Silver (Ag) | mg/L | 5 | ND | 0.01 | 3168265 |  | 5 | <0.01 | 0.01 | 4208707 | Y
Total Tin (Sn) | mg/L | 5 | ND | 0.2 | 3168265 |  | 5 | <0.02 | 0.02 | 4208707 | Y
Total Titanium (Ti) | mg/L | 5 | ND | 0.01 | 3168265 |  | 5 | <0.005 | 0.005 | 4208707 | Y
Total Zinc (Zn) | mg/L | 2 | 0.05 | 0.01 | 3168265 | Y | 2 | 0.097 | 0.005 | 4208707 | Y
SEMI-VOLATILE ORGANICS BY GC-MS (WATER)
Semivolatile Organics
Di-N-butyl phthalate | ug/L | 80 | ND | 8 | 3161611 |  | 80 | <10 | 10 | 4211698 | Y
Bis(2-ethylhexyl)phthalate | ug/L | 12 | ND | 8 | 3161611 |  | 12 | <10 | 10 | 4211698 | Y
3,3'-Dichlorobenzidine | ug/L | 2 | ND | 3 | 3161611 |  | 2 | <4 | 4 | 4211698 | Y
Pentachlorophenol | ug/L | 5 | ND | 4 | 3161611 |  | 5 | <5 | 5 | 4211698 | Y
Phenanthrene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Anthracene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Fluoranthene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Pyrene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Benzo(a)anthracene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Chrysene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Benzo(b/j)fluoranthene | ug/L | - | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Benzo(k)fluoranthene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Benzo(a)pyrene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Indeno(1,2,3-cd)pyrene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Dibenz(a,h)anthracene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Benzo(g,h,i)perylene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Dibenzo(a,i)pyrene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Benzo(e)pyrene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Perylene | ug/L | 5 | ND | 0.8 | 3161611 |  | NV | <1 | 1 | 4211698
Dibenzo(a,j) acridine | ug/L | 5 | ND | 2 | 3161611 |  | NV | <2 | 2 | 4211698
7H-Dibenzo(c,g) Carbazole | ug/L | 5 | ND | 2 | 3161611 |  | NV | <2 | 2 | 4211698
1,6-Dinitropyrene | ug/L | 5 | ND | 2 | 3161611 |  | NV | <2 | 2 | 4211698
1,3-Dinitropyrene | ug/L | - | ND | 2 | 3161611 |  | NV | <2 | 2 | 4211698
1,8-Dinitropyrene | ug/L | - | ND | 2 | 3161611 |  | NV | <2 | 2 | 4211698
Calculated Parameters
Total PAHs (18 PAHs) | ug/L | 5 | ND | 5 | 3159224 |  | 5 | <6 | 6 | 4205057 | Y
Surrogate Recovery (%)
2,4,6-Tribromophenol | % | - | 94 |  | 3161611 |  |  |  |  | 4211698
2-Fluorobiphenyl | % | - | 64 |  | 3161611 |  |  |  |  | 4211698
D14-Terphenyl (FS) | % | - | 84 |  | 3161611 |  |  |  |  | 4211698
D5-Nitrobenzene | % | - | 59 |  | 3161611 |  |  |  |  | 4211698
D8-Acenaphthylene | % | - | 72 |  | 3161611 |  |  |  |  | 4211698
VOLATILE OGANICS BY GC/MS (WATER)
Volatile Organics
Benzene | ug/L | 10 | ND | 0.1 | 3161040 |  | 10 | <2.5 | 2.5 | 4207783 | Y
Chloroform | ug/L | 40 | 1.5 | 0.1 | 3161040 | Y | 40 | 4.4 | 2.5 | 4207783 | Y
1,2-Dichlorobenzene | ug/L | 50 | ND | 0.2 | 3161040 |  | 50 | <5.0 | 5 | 4207783 | Y
1,4-Dichlorobenzene | ug/L | 80 | ND | 0.2 | 3161040 |  | 80 | <5.0 | 5 | 4207783 | Y
cis-1,2-Dichloroethylene | ug/L | 4000 | ND | 0.1 | 3161040 |  | 4000 | <2.5 | 2.5 | 4207783 | Y
trans-1,3-Dichloropropene | ug/L | 140 | ND | 0.2 | 3161040 |  | 140 | <5.0 | 5 | 4207783 | Y
Ethylbenzene | ug/L | 160 | ND | 0.1 | 3161040 |  | 160 | 62 | 2.5 | 4207783 | Y
Methylene Chloride(Dichloromethane) | ug/L | 2000 | ND | 0.5 | 3161040 |  | 2000 | <13 | 13 | 4207783 | Y
1,1,2,2-Tetrachloroethane | ug/L | 1400 | ND | 0.2 | 3161040 |  | 1400 | <5.0 | 5 | 4207783 | Y
Tetrachloroethylene | ug/L | 1000 | ND | 0.1 | 3161040 |  | 1000 | <2.5 | 2.5 | 4207783 | Y
Toluene | ug/L | 16 | ND | 0.2 | 3161040 |  | 16 | <5.0 | 5 | 4207783 | Y
Trichloroethylene | ug/L | 400 | ND | 0.1 | 3161040 |  | 400 | <2.5 | 2.5 | 4207783 | Y
p+m-Xylene | ug/L | 1400 | 0.13 | 0.1 | 3161040 | Y | NV | 250 | 2.5 | 4207783
o-Xylene | ug/L | 1400 | ND | 0.1 | 3161040 |  | NV | 59 | 2.5 | 4207783
Total Xylenes | ug/L | 1400 | 0.13 | 0.1 | 3161040 | Y | 1400 | 310 | 2.5 | 4207783 | Y
Surrogate Recovery (%)
4-Bromofluorobenzene | % | - | 100 |  | 3161040 |  |  |  |  | 4207783
D4-1,2-Dichloroethane | % | - | 96 |  | 3161040 |  |  |  |  | 4207783
D8-Toluene | % | - | 107 |  | 3161040 |  |  |  |  | 4207783
ORGANOCHLORINATED PESTICIDES BY GC-ECD (WATER)
Pesticides & Herbicides
Aldrin | ug/L | 0.2 | ND | 0.05 | 3161925 |  | NV | <0.005 | 0.005 | 4207258
Dieldrin | ug/L | 0.2 | ND | 0.06 | 3161925 |  | NV | <0.005 | 0.005 | 4207258
Aldrin + Dieldrin | ug/L | - | ND | 0.06 | 3161925 |  | 0.2 | <0.005 | 0.005 | 4204818 | Y
a-Chlordane | ug/L | 100 | ND | 0.05 | 3161925 |  | NV | <0.005 | 0.005 | 4207258
g-Chlordane | ug/L | 100 | ND | 0.1 | 3161925 |  | NV | <0.005 | 0.005 | 4207258
Chlordane (Total) | ug/L | 100 | ND | 0.1 | 3161925 |  | 100 | <0.005 | 0.005 | 4204818 | Y
o,p-DDT | ug/L | 0.1 | ND | 0.05 | 3161925 |  | NV | <0.005 | 0.005 | 4207258
p,p-DDT | ug/L | 0.1 | ND | 0.2 | 3161925 |  | NV | <0.005 | 0.005 | 4207258
o,p-DDT + p,p-DDT | ug/L | - | ND | 0.2 | 3161925 |  | 0.1 | <0.005 | 0.005 | 4204818 | Y
Lindane | ug/L | 100 | ND | 0.05 | 3161925 |  | 100 | <0.003 | 0.003 | 4207258 | Y
Hexachlorobenzene | ug/L | 0.1 | ND | 0.05 | 3161925 |  | 0.1 | <0.005 | 0.005 | 4207258 | Y
Total PCB | ug/L | 1 | ND | 0.5 | 3161925 |  | 1 | <0.05 | 0.05 | 4204818 | Y
Mirex | ug/L | 100 | ND | 0.3 | 3161925 |  | 100 | <0.005 | 0.005 | 4207258 | Y
Surrogate Recovery (%)
2,4,5,6-Tetrachloro-m-xylene | % | - | 78 |  | 3161925 |  |  |  |  | 4207258
Decachlorobiphenyl | % | - | 95 |  | 3161925 |  |  |  |  | 4207258
Glycols
Diethylene Glycol | mg/L
Ethylene Glycol | mg/L |  | ND | 5 | 3160338
Propylene Glycol | mg/L
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value

## BRL
Sampling Location, Date:
|  | BRL, 4/2/2013 |  |  |  |  | BRL, 9/17/2015
Sample Components | Unit | Bylaw | Result | RDL | RC Batch | Compliance(Y/N) | Bylaw | Result | RDL | RC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Calculated Parameters
Total Animal/Vegetable Oil and Grease | mg/L | 15 | 51 | 0.5 | 3169455 | N
Demand Parameters
Biochemical Oxygen Demand | mg/L | 500 | 360 | 2 | 3170867 | Y | 500 | 415 | 6 | 8042601 | Y | Y
Misc. Inorganics
Strong Acid Dissoc. Cyanide (CN) | mg/L | - | ND | 0.005 | 3171958 |  | 1 | 0.00378 | 0.0005 | 8045121 | Y
Fluoride (F-) | mg/L | - | ND | 0.1 | 3171828
Total Kjeldahl Nitrogen (TKN) | mg/L | - | 150 | 20 | 3176702 | Y
pH | pH | 5.5:10.5 | 8.36 |  | 3171829 | Y | 5.5:10.5 | 8.7 |  |  | Y
Phenols-4AAP | mg/L | 1 | 0.075 | 0.001 | 3220713 | Y
Anions
Dissolved Sulphate (SO4) | mg/L | 1500 | 19 | 1 | 3171817 | Y | 1500 | 13.6 | 0.5 | 8045961 | Y
Oil & Grease
Total Oil and grease | mg/L | 150 | 53 | 0.5 | 3171955 | Y | 150 | 8.4 | 1 | 8044772 | Y
Oil & Grease (mineral/synthetic) | mg/L | - | 1.8 | 0.5 | 3172010 | Y | 15 | <2.0 | 2 | 8044780 | Y
Physical Properties
Total Suspended Solids | mg/L | 600 | 390 | 100 | 3172143 | Y | 600 | 511 | 7 | 8046144 | Y | Y
SEMIVOLATILE ORGANICS BY GC-MS (WATER)
SEMI-VOLATILE ORGANICS
Phenol | ug/L | [5 empty] | 1000 | 50 | 2.5 | 8044702 | Y
2-chlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
3 & 4-chlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2-methylphenol | ug/L | [5 empty] | NV | <2.5 | 2.5 | 8044702
3 & 4-methylphenol | ug/L | [5 empty] | NV | 120 | 2.5 | 8044702
2-nitrophenol | ug/L | [5 empty] | NV | <2.50 | 2.5 | 8044702
2,4-dimethylphenol | ug/L | [5 empty] | NV | <2.5 | 2.5 | 8044702
2,4 + 2,5-Dichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,3-Dichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,6-dichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
3,5-Dichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
3,4-Dichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,4,5-trichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,4,6-trichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,3,5-trichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,3,6-Trichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,3,4-trichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
3,4,5-Trichlorophenol | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044702
2,4-dinitrophenol | ug/L | [5 empty] | NV | <2.5 | 2.5 | 8044702
4,6-dinitro-2-methylphenol | ug/L | [5 empty] | NV | <2.5 | 2.5 | 8044702
2,3,4,6-tetrachlorophenol | ug/L | 50 | ND | 30 | 3173331 |  | 50 | <0.50 | 0.5 | 8044702 | Y
2,3,4,5-tetrachlorophenol | ug/L | 50 | ND | 20 | 3173331 |  | 50 | <0.50 | 0.5 | 8044702 | Y
2,3,5,6-tetrachlorophenol | ug/L | 50 | ND | 30 | 3173331 |  | 50 | <0.50 | 0.5 | 8044702 | Y
4-nitrophenol | ug/L | [5 empty] | NV | <2.5 | 2.5 | 8044702
2,6-Dimethylphenol | ug/L | [5 empty] | NV | <2.5 | 2.5 | 8044702
3,4-Dimethylphenol | ug/L | [5 empty] | NV | <2.5 | 2.5 | 8044702
Pentachlorophenol | ug/L | 50 | ND | 50 | 3173331 |  | 50 | <0.50 | 0.5 | 8044702 | Y
Surrogate Recovery (%)
2,4,6-Tribromophenol | % | - | 85 |  | 3173331 |  |  |  | 105 | 8044702
2,4-DIBROMOPHENOL | % | [7 empty] | 92 | 8044702
MISCELLANEOUS (WATER)
Sulphide | mg/L | 1 | 0.16 | 0.02 | 3172860 | Y | 1 | 0.101 | 0.005 | 8047776 | Y
LEPH & HEPH WITH CSR PAH IN WATER (WATER)
Polycyclic Aromatics
Low Molecular Weight PAH`s | ug/L | [5 empty] | 50 | 0.27 | 0.24 | 8042168 | Y
High Molecular Weight PAH`s | ug/L | [5 empty] | 50 | <0.063 | 0.063 | 8042168 | Y
Total PAH | ug/L | 50 | ND | 40 | 3169456 |  | 50 | 0.27 | 0.24 | 8042168 | Y
Naphthalene | ug/L | - | ND | 10 | 3173331 |  | 50 | 0.22 | 0.1 | 8046160 | Y
2-Methylnaphthalene | ug/L | [5 empty] | NV | <0.10 | 0.1 | 8046160
Quinoline | ug/L | [5 empty] | NV | <0.24 | 0.24 | 8046160
Acenaphthylene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.050 | 0.05 | 8046160 | Y
Acenaphthene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.053 | 0.053 | 8046160 | Y
Fluorene | ug/L | - | ND | 10 | 3173331 |  | 50 | 0.055 | 0.05 | 8046160 | Y
Phenanthrene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.21 | 0.21 | 8046160 | Y
Anthracene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.010 | 0.01 | 8046160 | Y
Acridine | ug/L | [5 empty] | NV | <0.050 | 0.05 | 8046160
Fluoranthene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.063 | 0.063 | 8046160 | Y
Pyrene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.020 | 0.02 | 8046160 | Y
Benzo(a)anthracene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.028 | 0.028 | 8046160 | Y
Chrysene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.050 | 0.05 | 8046160 | Y
Benzo(b&j)fluoranthene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.050 | 0.05 | 8046160 | Y
Benzo(k)fluoranthene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.050 | 0.05 | 8046160 | Y
Benzo(a)pyrene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.0090 | 0.009 | 8046160 | Y
Indeno(1,2,3-cd)pyrene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.050 | 0.05 | 8046160 | Y
Dibenz(a,h)anthracene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.050 | 0.05 | 8046160 | Y
Benzo(g,h,i)perylene | ug/L | - | ND | 10 | 3173331 |  | 50 | <0.050 | 0.05 | 8046160 | Y
Surrogate Recovery (%)
2-Fluorobiphenyl | % | - | 70 |  | 3173331
2-Fluorophenol | % | - | 40 |  | 3173331
D14-Terphenyl | % | - | 65 |  | 3173331
D5-Nitrobenzene | % | - | 65 |  | 3173331
D5-Phenol | % | - | 35 |  | 3173331
O-TERPHENYL (sur.) | % | [6 empty] | 109 |  | 8046173
D10-ANTHRACENE (sur.) | % | [6 empty] | 116 |  | 8046160
D8-ACENAPHTHYLENE (sur.) | % | [6 empty] | 104 |  | 8046160
D8-NAPHTHALENE (sur.) | % | [6 empty] | 112 |  | 8046160
D9-Acridine | % | [6 empty] | 100 |  | 8046160
TERPHENYL-D14 (sur.) | % | [6 empty] | 107 |  | 8046160
Calculated Parameters
LEPH (C10-C19 less PAH)6 | mg/L | [5 empty] | 15 | 0.35 | 0.2 | 8042169 | Y
HEPH (C19-C32 less PAH)6 | mg/L | [5 empty] | 15 | 8.5 | 0.2 | 8042169 | Y
Nonylphenol Ethoxylate (Total) | mg/L | - | 0.12 | 0.025 | 3172702 | Y
Nonylphenol (Total) | mg/L | - | 0.001 | 0.001 | 3172701 | Y
Ext. Pet. Hydrocarbon
EPH (C10-C19)6 | mg/L | [5 empty] | 15 | 0.35 | 0.2 | 8046173 | Y
EPH (C19-C32)6 | mg/L | [5 empty] | 15 | 8.5 | 0.2 | 8046173 | Y
Calculated Parameters
Total Hardness (CaCO3) | mg/L | [5 empty] | NV | 48.4 | 0.5 | 8042180
Elements
Total Mercury (Hg) | ug/L | 0.05 | ND | 0.0001 | 3175844 |  | 50 | <0.010 | 0.01 | 8049496 | Y
Total Metals by ICPMS
Total Aluminum (Al) | mg/L | 50 | 0.4 | 0.1 | 3176388 | Y | 50 | 0.151 | 0.003 | 8046380 | Y
Total Antimony (Sb) | mg/L | - | ND | 0.2 | 3176388 |  | NV | <0.00050 | 0.0005 | 8046380
Total Arsenic (As) | mg/L | 1 | ND | 0.2 | 3176388 |  | 1 | 0.00047 | 0.0001 | 8046380 | Y
Total Barium (Ba) | mg/L | [5 empty] | NV | 0.0202 | 0.001 | 8046380
Total Beryllium (Be) | mg/L | [5 empty] | NV | <0.00010 | 0.0001 | 8046380
Total Bismuth (Bi) | mg/L | [5 empty] | NV | <0.0010 | 0.001 | 8046380
Total Boron (B) | mg/L | [5 empty] | 50 | 0.063 | 0.05 | 8046380 | Y
Total Cadmium (Cd) | mg/L | 0.2 | ND | 0.005 | 3176388 |  | 0.2 | 0.000228 | 1e-05 | 8046380 | Y
Total Chromium (Cr) | mg/L | 4 | ND | 0.01 | 3176388 |  | 4 | 0.0017 | 0.001 | 8046380 | Y
Chromium (VI) | mg/L | - | ND | 0.5 | 3172235
Total Cobalt (Co) | mg/L | 5 | ND | 0.02 | 3176388 |  | 5 | <0.00050 | 0.0005 | 8046380 | Y
Total Copper (Cu) | mg/L | 2 | 0.29 | 0.02 | 3176388 | Y | 2 | 0.154 | 0.0005 | 8046380 | Y
Total Iron (Fe) | mg/L | [5 empty] | 10 | 1.08 | 0.01 | 8046380 | Y
Total Lead (Pb) | mg/L | 1 | ND | 0.05 | 3176388 |  | 1 | 0.00204 | 0.0002 | 8046380 | Y
Total Lithium (Li) | mg/L | [5 empty] | NV | <0.0050 | 0.005 | 8046380
Total Manganese (Mn) | mg/L | 5 | 0.09 | 0.01 | 3176388 | Y | 5 | 0.058 | 0.001 | 8046380 | Y
Total Molybdenum (Mo) | mg/L | 1 | ND | 0.02 | 3176388 |  | 1 | 0.0025 | 0.001 | 8046380 | Y
Total Nickel (Ni) | mg/L | 2 | ND | 0.05 | 3176388 |  | 2 | 0.0055 | 0.001 | 8046380 | Y
Total Phosphorus (P) | mg/L | - | 15 | 0.1 | 3176388 | Y
Total Selenium (Se) | mg/L | 1 | ND | 0.2 | 3176388 |  | 1 | 0.00092 | 0.0001 | 8046380 | Y
Total Silicon (Si) | mg/L | 1 | ND | 0.01 | 3176388 |  | NV | 2.19 | 0.1 | 8046380
Total Silver (Ag) | mg/L | [5 empty] | 1 | 6.2e-05 | 2e-05 | 8046380 | Y
Total Strontium (Sr) | mg/L | [5 empty] | NV | 0.0382 | 0.001 | 8046380
Total Thallium (Tl) | mg/L | [5 empty] | NV | <0.000050 | 5e-05 | 8046380
Total Tin (Sn) | mg/L | - | ND | 0.2 | 3176388 |  | NV | <0.0050 | 0.005 | 8046380
Total Titanium (Ti) | mg/L | - | ND | 0.01 | 3176388 |  | NV | <0.0050 | 0.005 | 8046380
Total Uranium (U) | mg/L | [5 empty] | NV | <0.00010 | 0.0001 | 8046380
Total Vanadium (V) | mg/L | [5 empty] | NV | <0.0050 | 0.005 | 8046380
Total Zinc (Zn) | mg/L | 3 | 0.27 | 0.01 | 3176388 | Y | 3 | 0.182 | 0.005 | 8046380 | Y
Total Zirconium (Zr) | mg/L | [5 empty] | NV | 0.00077 | 0.0005 | 8046380
Total Calcium (Ca) | mg/L | [5 empty] | NV | 13.5 | 0.05 | 8042183
Total Magnesium (Mg) | mg/L | [5 empty] | NV | 3.53 | 0.05 | 8042183
Total Potassium (K) | mg/L | [5 empty] | NV | 42.8 | 0.05 | 8042183
Total Sodium (Na) | mg/L | [5 empty] | NV | 40.9 | 0.05 | 8042183
Total Sulphur (S) | mg/L | [5 empty] | NV | 10.9 | 3 | 8042183
Volatiles
VPH (VHW6 to 10 - BTEX) | ug/L | [5 empty] | NV | <300 | 300 | 8042171
Chloromethane | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
Vinyl chloride | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
Chloroethane | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
Trichlorofluoromethane | ug/L | [5 empty] | NV | <4.0 | 4 | 8044829
1,1-dichloroethene | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
Dichloromethane | ug/L | 2000 | ND | 25 | 3172091 |  | NV | <2.0 | 2 | 8044829
trans-1,2-dichloroethene | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
1,1-dichloroethane | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
cis-1,2-dichloroethene | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
cis-1,2-Dichloroethylene | ug/L | 4000 | ND | 5 | 3172091
Chloroform | ug/L | 40 | 6.2 | 5 | 3172091 | Y | NV | 9.8 | 1 | 8044829
1,1,1-trichloroethane | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
1,2-dichloroethane | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
Carbon tetrachloride | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
Benzene | ug/L | 10 | ND | 5 | 3172091 |  | 1000 | <0.40 | 0.4 | 8044829 | Y
Methyl-tert-butylether (MTBE) | ug/L | [5 empty] | NV | <4.0 | 4 | 8044829
1,2-dichloropropane | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
cis-1,3-dichloropropene | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
trans-1,3-dichloropropene | ug/L | 140 | ND | 10 | 3172091 |  | NV | <1.0 | 1 | 8044829
Bromomethane | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
1,1,2-trichloroethane | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
Trichloroethene | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
Trichloroethylene | ug/L | 400 | ND | 5 | 3172091
Chlorodibromomethane | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
1,2-dibromoethane | ug/L | [5 empty] | NV | <0.20 | 0.2 | 8044829
Tetrachloroethene | ug/L | [5 empty] | 50 | <0.50 | 0.5 | 8044829 | Y
Tetrachloroethylene | ug/L | 1000 | ND | 5 | 3172091
Bromodichloromethane | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
Toluene | ug/L | 16 | ND | 10 | 3172091 |  | 1000 | <0.40 | 0.4 | 8044829 | Y
Ethylbenzene | ug/L | 160 | ND | 5 | 3172091 |  | 1000 | <0.40 | 0.4 | 8044829 | Y
m & p-Xylene | ug/L | 1400 | ND | 5 | 3172091 |  | NV | <0.40 | 0.4 | 8044829
Bromoform | ug/L | [5 empty] | NV | <1.0 | 1 | 8044829
Styrene | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
o-Xylene | ug/L | 1400 | ND | 5 | 3172091 |  | NV | <0.40 | 0.4 | 8044829
Xylenes (Total) | ug/L | 1400 | ND | 5 | 3172091 |  | 1000 | <0.40 | 0.4 | 8044829 | Y
1,1,1,2-tetrachloroethane | ug/L | 1400 | ND | 10 | 3172091 |  | NV | <0.50 | 0.5 | 8044829
1,1,2,2-tetrachloroethane | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
1,2-dichlorobenzene | ug/L | 50 | ND | 10 | 3172091 |  | NV | <0.50 | 0.5 | 8044829
1,3-dichlorobenzene | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
1,4-dichlorobenzene | ug/L | 80 | 11 | 10 | 3172091 | Y | NV | <0.50 | 0.5 | 8044829
Chlorobenzene | ug/L | [5 empty] | NV | <0.50 | 0.5 | 8044829
VH C6-C10 | ug/L | [5 empty] | NV | <300 | 300 | 8044829
Surrogate Recovery (%)
4-Bromofluorobenzene | % | - | 97 |  | 3172091 |  |  | 75 |  | 8044829
D4-1,2-Dichloroethane | % | - | 90 |  | 3172091 |  |  | 88 |  | 8044829
1,4-Difluorobenzene (sur.) | [7 empty] | 98 |  | 8044829
D8-Toluene | % | - | 92 |  | 3172091
ORGANOCHLORINATED PESTICIDES BY GC-ECD (WATER)
Pesticides & Herbicides
Aldrin | ug/L | 0.2 | ND | 0.05 | 3171806
Dieldrin | ug/L | 0.2 | ND | 0.05 | 3171806
Aldrin + Dieldrin | ug/L | - | ND | 0.05 | 3171806
a-Chlordane | ug/L | 100 | ND | 0.05 | 3171806
g-Chlordane | ug/L | 100 | ND | 0.05 | 3171806
Chlordane (Total) | ug/L | 100 | ND | 0.05 | 3171806
o,p-DDT | ug/L | 0.1 | ND | 0.05 | 3171806
p,p-DDT | ug/L | 0.1 | ND | 0.05 | 3171806
o,p-DDT + p,p-DDT | ug/L | - | ND | 0.05 | 3171806
Lindane | ug/L | 100 | ND | 0.03 | 3171806
Hexachlorobenzene | ug/L | 0.1 | ND | 0.05 | 3171806
Total PCB | ug/L | 1 | ND | 0.5 | 3171806
Mirex | ug/L | 100 | ND | 0.05 | 3171806
Surrogate Recovery (%)
2,4,5,6-Tetrachloro-m-xylene | % | - | 75 |  | 3171806
Decachlorobiphenyl | % | - | 67 |  | 3171806
ORGANOCHLORINATED PESTICIDES BY GC-ECD (WATER)
Glycols
Diethylene Glycol | mg/L |  | ND | 5 | 3174843
Ethylene Glycol | mg/L |  | ND | 5 | 3174843
Propylene Glycol | mg/L |  | ND | 5 | 3174843
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value
Note on I13: Hun, Riley: Field condition observation

## VRL
Sampling Location, Date
VRL, 09/18/2015
Sample Components | Units | Bylaw | Result | RDL | QC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Demand Parameters
Biochemical Oxygen Demand | mg/L | 500 | 178 | 6 | 8045044 | Y
Misc. Inorganics
Strong Acid Dissoc. Cyanide (CN) | mg/L | 1 | 0.00242 | 0.0005 | 8045121 | Y
Anions
Dissolved Sulphate (SO4) | mg/L | 1500 | 44.4 | 0.5 | 8046078 | Y
pH | pH | 5.5:10.5 | 7.01
Oil & Grease
Total Oil and grease | mg/L | 100 | 3.1 | 1 | 8047224 | Y
Oil & Grease (mineral/synthetic) | mg/L | 15 | <2.0 | 2 | 8047231 | Y
Physical Properties
Total Suspended Solids | mg/L | 350 | 78 | 10 | 8047668 | Y
SEMIVOLATILE ORGANICS BY GC-MS (WATER)
Semi-Volatile Organics
Phenol | ug/L | 1000 | 22 | 2.5 | 8046141 | Y
2-chlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
3 & 4-chlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2-methylphenol | ug/L | NV | <2.5 | 2.5 | 8046141
3 & 4-methylphenol | ug/L | NV | 27 | 2.5 | 8046141
2-nitrophenol | ug/L | NV | <2.5 | 2.5 | 8046141
2,4-dimethylphenol | ug/L | NV | <2.5 | 2.5 | 8046141
2,4 + 2,5-Dichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,3-Dichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,6-dichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
3,5-Dichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
3,4-Dichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,4,5-trichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,4,6-trichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,3,5-trichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,3,6-Trichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,3,4-trichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
3,4,5-Trichlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,4-dinitrophenol | ug/L | NV | <2.5 | 2.5 | 8046141
4,6-dinitro-2-methylphenol | ug/L | NV | <2.5 | 2.5 | 8046141
2,3,4,6-tetrachlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,3,4,5-tetrachlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
2,3,5,6-tetrachlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
4-nitrophenol | ug/L | NV | <2.5 | 2.5 | 8046141
2,6-Dimethylphenol | ug/L | NV | <2.5 | 2.5 | 8046141
3,4-Dimethylphenol | ug/L | NV | <2.5 | 2.5 | 8046141
Pentachlorophenol | ug/L | nd | <0.50 | 0.5 | 8046141
MISCELLANEOUS (WATER)
Sulphide | mg/L | 1 | 0.0452 | 0.005 | 8047776 | Y
Polycyclic Aromatics
Low Molecular Weight PAH`s | ug/L | 50 | <1.2 | 1.2 | 8044478 | Y
High Molecular Weight PAH`s | ug/L | 50 | <0.25 | 0.25 | 8044478 | Y
Total PAH | ug/L | 50 | <1.2 | 1.2 | 8044478 | Y
Naphthalene | ug/L | 50 | <0.50 | 0.5 | 8046786 | Y
2-Methylnaphthalene | ug/L | NV | <0.50 | 0.5 | 8046786
Quinoline | ug/L | NV | <1.2 | 1.2 | 8046786
Acenaphthylene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Acenaphthene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Fluorene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Phenanthrene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Anthracene | ug/L | 50 | <0.050 | 0.05 | 8046786 | Y
Acridine | ug/L | NV | <0.25 | 0.25 | 8046786
Fluoranthene | ug/L | 50 | <0.10 | 0.1 | 8046786 | Y
Pyrene | ug/L | 50 | <0.10 | 0.1 | 8046786 | Y
Benzo(a)anthracene | ug/L | 50 | <0.050 | 0.05 | 8046786 | Y
Chrysene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Benzo(b&j)fluoranthene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Benzo(k)fluoranthene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Benzo(a)pyrene | ug/L | 50 | <0.045 | 0.045 | 8046786 | Y
Indeno(1,2,3-cd)pyrene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Dibenz(a,h)anthracene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Benzo(g,h,i)perylene | ug/L | 50 | <0.25 | 0.25 | 8046786 | Y
Calculated Parameters
LEPH (C10-C19 less PAH)6 | mg/L | 15 | 0.43 | 0.2 | 8044480 | Y
HEPH (C19-C32 less PAH)6 | mg/L | 15 | 5.4 | 0.2 | 8044480 | Y
Ext. Pet. Hydrocarbon
EPH (C10-C19)6 | mg/L | 15 | 0.43 | 0.2 | 8046791 | Y
EPH (C19-C32)6 | mg/L | 15 | 5.4 | 0.2 | 8046791 | Y
Surrogate Recovery (%)
O-TERPHENYL (sur.) | % |  | 99 |  | 8046791
D10-ANTHRACENE (sur.) | % |  | 108 |  | 8046786
D8-ACENAPHTHYLENE (sur.) | % |  | 104 |  | 8046786
D8-NAPHTHALENE (sur.) | % |  | 102 |  | 8046786
D9-Acridine | % |  | 90 |  | 8046786
TERPHENYL-D14 (sur.) | % |  | 115 |  | 8046786
Calculated Parameters
Total Hardness (CaCO3) | mg/L | NV | 45.7 | 0.5 | 8044475
Elements
Total Mercury (Hg) | ug/L | 20 | <0.010 | 0.01 | 8050474 | Y
Total Metals by ICPMS
Total Aluminum (Al) | mg/L | NV | 0.0818 | 0.003 | 8046380
Total Antimony (Sb) | mg/L | NV | <0.00050 | 0.0005 | 8046380
Total Arsenic (As) | mg/L | 0.4 | 0.00029 | 0.0001 | 8046380 | Y
Total Barium (Ba) | mg/L | NV | 0.0065 | 0.001 | 8046380
Total Beryllium (Be) | mg/L | NV | <0.00010 | 0.0001 | 8046380
Total Bismuth (Bi) | mg/L | NV | <0.0010 | 0.001 | 8046380
Total Boron (B) | mg/L | NV | 0.375 | 0.05 | 8046380
Total Cadmium (Cd) | mg/L | 0.3 | 9.7e-05 | 1e-05 | 8046380 | Y
Total Chromium (Cr) | mg/L | 4 | <0.0010 | 0.001 | 8046380 | Y
Total Cobalt (Co) | mg/L | 5 | <0.00050 | 0.0005 | 8046380 | Y
Total Copper (Cu) | mg/L | 1 | 0.416 | 0.0005 | 8046380 | Y
Total Iron (Fe) | mg/L | 50 | 0.796 | 0.01 | 8046380 | Y
Total Lead (Pb) | mg/L | 1 | 0.00198 | 0.0002 | 8046380 | Y
Total Lithium (Li) | mg/L | NV | <0.0050 | 0.005 | 8046380
Total Manganese (Mn) | mg/L | 5 | 0.0314 | 0.001 | 8046380 | Y
Total Molybdenum (Mo) | mg/L | 5 | <0.0010 | 0.001 | 8046380 | Y
Total Nickel (Ni) | mg/L | 3 | 0.0024 | 0.001 | 8046380 | Y
Total Selenium (Se) | mg/L | 0.3 | 0.00038 | 0.0001 | 8046380 | Y
Total Silicon (Si) | mg/L | NV | 3.38 | 0.1 | 8046380
Total Silver (Ag) | mg/L | 0.5 | 3.1e-05 | 2e-05 | 8046380 | Y
Total Strontium (Sr) | mg/L | NV | 0.0355 | 0.001 | 8046380
Total Thallium (Tl) | mg/L | NV | <0.000050 | 5e-05 | 8046380
Total Tin (Sn) | mg/L | NV | <0.0050 | 0.005 | 8046380
Total Titanium (Ti) | mg/L | NV | <0.0050 | 0.005 | 8046380
Total Uranium (U) | mg/L | NV | <0.00010 | 0.0001 | 8046380
Total Vanadium (V) | mg/L | NV | <0.0050 | 0.005 | 8046380
Total Zinc (Zn) | mg/L | 3 | 0.0788 | 0.005 | 8046380 | Y
Total Zirconium (Zr) | mg/L | NV | <0.00050 | 0.0005 | 8046380
Total Calcium (Ca) | mg/L | NV | 12.3 | 0.05 | 8044476
Total Magnesium (Mg) | mg/L | NV | 3.64 | 0.05 | 8044476
Total Potassium (K) | mg/L | NV | 27.8 | 0.05 | 8044476
Total Sodium (Na) | mg/L | NV | 50.1 | 0.05 | 8044476
Total Sulphur (S) | mg/L | NV | 18.2 | 3 | 8044476
Volatiles
VPH (VHW6 to 10 - BTEX) | ug/L | NV | <300 | 300 | 8044481
Chloromethane | ug/L | NV | <1.0 | 1 | 8046486
Vinyl chloride | ug/L | NV | <0.50 | 0.5 | 8046486
Chloroethane | ug/L | NV | <1.0 | 1 | 8046486
Trichlorofluoromethane | ug/L | NV | <4.0 | 4 | 8046486
1,1-dichloroethene | ug/L | NV | <0.50 | 0.5 | 8046486
Dichloromethane | ug/L | NV | <2.0 | 2 | 8046486
trans-1,2-dichloroethene | ug/L | NV | <1.0 | 1 | 8046486
1,1-dichloroethane | ug/L | NV | <0.50 | 0.5 | 8046486
cis-1,2-dichloroethene | ug/L | NV | <1.0 | 1 | 8046486
Chloroform | ug/L | NV | 9.6 | 1 | 8046486
1,1,1-trichloroethane | ug/L | NV | <0.50 | 0.5 | 8046486
1,2-dichloroethane | ug/L | NV | <0.50 | 0.5 | 8046486
Carbon tetrachloride | ug/L | NV | <0.50 | 0.5 | 8046486
Benzene | ug/L | 100 | <0.40 | 0.4 | 8046486 | Y
Methyl-tert-butylether (MTBE) | ug/L | NV | <4.0 | 4 | 8046486
1,2-dichloropropane | ug/L | NV | <0.50 | 0.5 | 8046486
cis-1,3-dichloropropene | ug/L | NV | <1.0 | 1 | 8046486
trans-1,3-dichloropropene | ug/L | NV | <1.0 | 1 | 8046486
Bromomethane | ug/L | NV | <1.0 | 1 | 8046486
1,1,2-trichloroethane | ug/L | NV | <0.50 | 0.5 | 8046486
Trichloroethene | ug/L | NV | <0.50 | 0.5 | 8046486
Chlorodibromomethane | ug/L | NV | <1.0 | 1 | 8046486
1,2-dibromoethane | ug/L | NV | <0.20 | 0.2 | 8046486
Tetrachloroethene | ug/L | nd | <0.50 | 0.5 | 8046486
Bromodichloromethane | ug/L | NV | 1.6 | 1 | 8046486
Toluene | ug/L | 200 | <0.40 | 0.4 | 8046486 | Y
Ethylbenzene | ug/L | 200 | <0.40 | 0.4 | 8046486 | Y
m & p-Xylene | ug/L | NV | <0.40 | 0.4 | 8046486
Bromoform | ug/L | NV | <1.0 | 1 | 8046486
Styrene | ug/L | NV | <0.50 | 0.5 | 8046486
o-Xylene | ug/L | NV | <0.40 | 0.4 | 8046486
Xylenes (Total) | ug/L | 200 | <0.40 | 0.4 | 8046486 | Y
1,1,1,2-tetrachloroethane | ug/L | NV | <0.50 | 0.5 | 8046486
1,1,2,2-tetrachloroethane | ug/L | NV | <0.50 | 0.5 | 8046486
1,2-dichlorobenzene | ug/L | NV | <0.50 | 0.5 | 8046486
1,3-dichlorobenzene | ug/L | NV | <0.50 | 0.5 | 8046486
1,4-dichlorobenzene | ug/L | NV | <0.50 | 0.5 | 8046486
Chlorobenzene | ug/L | NV | <0.50 | 0.5 | 8046486
VH C6-C10 | ug/L | NV | <300 | 300 | 8046486
Surrogate Recovery (%)
1,4-Difluorobenzene (sur.) | % |  | 100 |  | 8046486
4-Bromofluorobenzene (sur.) | % |  | 86 |  | 8046486
D4-1,2-Dichloroethane (sur.) | % |  | 92 |  | 8046486
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value
Note on D11: Hun, Riley: Field condition observation

## Surrey
Sampling Location/Date
Surrey, 9/17/2015
Sample Components | Units | Bylaw | Result | RDL | RC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Demand Parameters
Biochemical Oxygen Demand | mg/L | 500 | 199 | 6 | 8042601 | Y
Misc. Inorganics
Strong Acid Dissoc. Cyanide (CN) | mg/L | 1 | 0.00574 | 0.0005 | 8045121 | Y
pH | pH | 5.5 to 10.0 | 7.04
Anions
Dissolved Sulphate (SO4) | mg/L | 1500 | 21 | 0.5 | 8045961 | Y
Oil & Grease
Total Oil and grease | mg/L | 150 | 10 | 1 | 8044772 | Y
Oil & Grease (mineral/synthetic) | mg/L | 15 | <2.0 | 2 | 8044780 | Y
Physical Properties
Total Suspended Solids | mg/L | 600 | 27.8 | 1 | 8046144 | Y
SEMIVOLATILE ORGANICS BY GC-MS (WATER)
Semi-Volatile Organics
Phenol | ug/L | 1000 | 1.6 | 0.5 | 8044702 | Y
2-chlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
3 & 4-chlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
2-methylphenol | ug/L | NV | <0.50 | 0.5 | 8044702
3 & 4-methylphenol | ug/L | NV | 2.5 | 0.5 | 8044702
2-nitrophenol | ug/L | NV | <0.50 | 0.5 | 8044702
2,4-dimethylphenol | ug/L | NV | <0.50 | 0.5 | 8044702
2,4 + 2,5-Dichlorophenol | ug/L | NV | 0.2 | 0.1 | 8044702
2,3-Dichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
2,6-dichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
3,5-Dichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
3,4-Dichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
2,4,5-trichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
2,4,6-trichlorophenol | ug/L | NV | 0.68 | 0.1 | 8044702
2,3,5-trichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
2,3,6-Trichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
2,3,4-trichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
3,4,5-Trichlorophenol | ug/L | NV | <0.10 | 0.1 | 8044702
2,4-dinitrophenol | ug/L | NV | <0.50 | 0.5 | 8044702
4,6-dinitro-2-methylphenol | ug/L | NV | <0.50 | 0.5 | 8044702
2,3,4,6-tetrachlorophenol | ug/L | 50 | <0.10 | 0.1 | 8044702 | Y
2,3,4,5-tetrachlorophenol | ug/L | 50 | <0.10 | 0.1 | 8044702 | Y
2,3,5,6-tetrachlorophenol | ug/L | 50 | <0.10 | 0.1 | 8044702 | Y
4-nitrophenol | ug/L | NV | <1.0 | 1 | 8044702
2,6-Dimethylphenol | ug/L | NV | <0.50 | 0.5 | 8044702
3,4-Dimethylphenol | ug/L | NV | <0.50 | 0.5 | 8044702
Pentachlorophenol | ug/L | 50 | <0.10 | 0.1 | 8044702 | Y
Surrogate Recovery (%)
2,4,6-TRIBROMOPHENOL (sur.) | % |  |  | 105 | 8044702
2,4-DIBROMOPHENOL | % |  |  | 92 | 8044702
MISCELLANEOUS (WATER)
Sulphide | mg/L | 1 | 0.0391 | 0.005 | 8047776 | Y
LEPH & HEPH WITH CSR PAH IN WATER (WATER)
Polycyclic Aromatics
Low Molecular Weight PAH`s | ug/L | 50 | 0.37 | 0.24 | 8042168 | Y
High Molecular Weight PAH`s | ug/L | 50 | <0.050 | 0.05 | 8042168 | Y
Total PAH | ug/L | 50 | 0.41 | 0.24 | 8042168 | Y
Naphthalene | ug/L | 50 | 0.18 | 0.1 | 8044759 | Y
2-Methylnaphthalene | ug/L | NV | <0.10 | 0.1 | 8044759
Quinoline | ug/L | NV | <0.24 | 0.24 | 8044759
Acenaphthylene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Acenaphthene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Fluorene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Phenanthrene | ug/L | 50 | 0.19 | 0.05 | 8044759 | Y
Anthracene | ug/L | 50 | <0.010 | 0.01 | 8044759 | Y
Acridine | ug/L | NV | <0.050 | 0.05 | 8044759
Fluoranthene | ug/L | 50 | 0.049 | 0.02 | 8044759 | Y
Pyrene | ug/L | 50 | <0.020 | 0.02 | 8044759 | Y
Benzo(a)anthracene | ug/L | 50 | <0.010 | 0.01 | 8044759 | Y
Chrysene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Benzo(b&j)fluoranthene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Benzo(k)fluoranthene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Benzo(a)pyrene | ug/L | 50 | <0.0090 | 0.009 | 8044759 | Y
Indeno(1,2,3-cd)pyrene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Dibenz(a,h)anthracene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Benzo(g,h,i)perylene | ug/L | 50 | <0.050 | 0.05 | 8044759 | Y
Calculated Parameters
LEPH (C10-C19 less PAH)6 | mg/L | 15 | 0.59 | 0.2 | 8042169 | Y
HEPH (C19-C32 less PAH)6 | mg/L | 15 | 1.2 | 0.2 | 8042169 | Y
Ext. Pet. Hydrocarbon
EPH (C10-C19)6 | mg/L | 15 | 0.59 | 0.2 | 8044796 | Y
EPH (C19-C32)6 | mg/L | 15 | 1.2 | 0.2 | 8044796 | Y
Surrogate Recovery (%)
O-TERPHENYL (sur.) | % |  | 105 |  | 8044796
D10-ANTHRACENE (sur.) | % |  | 103 |  | 8044759
D8-ACENAPHTHYLENE (sur.) | % |  | 99 |  | 8044759
D8-NAPHTHALENE (sur.) | % |  | 93 |  | 8044759
D9-Acridine | % |  | 80 |  | 8044759
TERPHENYL-D14 (sur.) | % |  | 110 |  | 8044759
Calculated Parameters
Total Hardness (CaCO3) | mg/L | NV | 13 | 0.5 | 8042180
Elements
Total Mercury (Hg) | ug/L | 50 | <0.010 | 0.01 | 8049496 | Y
Total Metals by ICPMS
Total Aluminum (Al) | mg/L | 50 | 0.0288 | 0.003 | 8045259 | Y
Total Antimony (Sb) | mg/L | NV | <0.00050 | 0.0005 | 8045259
Total Arsenic (As) | mg/L | 1 | 0.0001 | 0.0001 | 8045259 | Y
Total Barium (Ba) | mg/L | NV | 0.0046 | 0.001 | 8045259
Total Beryllium (Be) | mg/L | NV | <0.00010 | 0.0001 | 8045259
Total Bismuth (Bi) | mg/L | NV | <0.0010 | 0.001 | 8045259
Total Boron (B) | mg/L | 50 | 0.086 | 0.05 | 8045259 | Y
Total Cadmium (Cd) | mg/L | 0.2 | <0.000010 | 1e-05 | 8045259 | Y
Total Chromium (Cr) | mg/L | 4 | <0.0010 | 0.001 | 8045259 | Y
Total Cobalt (Co) | mg/L | 5 | <0.00050 | 0.0005 | 8045259 | Y
Total Copper (Cu) | mg/L | 2 | 0.0302 | 0.0005 | 8045259 | Y
Total Iron (Fe) | mg/L | 10 | 0.262 | 0.01 | 8045259 | Y
Total Lead (Pb) | mg/L | 1 | 0.00024 | 0.0002 | 8045259 | Y
Total Lithium (Li) | mg/L | NV | 0.0707 | 0.005 | 8045259
Total Manganese (Mn) | mg/L | 5 | 0.0091 | 0.001 | 8045259 | Y
Total Molybdenum (Mo) | mg/L | 1 | <0.0010 | 0.001 | 8045259 | Y
Total Nickel (Ni) | mg/L | 2 | <0.0010 | 0.001 | 8045259 | Y
Total Selenium (Se) | mg/L | 1 | 0.00014 | 0.0001 | 8045259 | Y
Total Silicon (Si) | mg/L | NV | 2.24 | 0.1 | 8045259
Total Silver (Ag) | mg/L | 1 | 9e-05 | 2e-05 | 8045259 | Y
Total Strontium (Sr) | mg/L | NV | 0.0126 | 0.001 | 8045259
Total Thallium (Tl) | mg/L | NV | <0.000050 | 5e-05 | 8045259
Total Tin (Sn) | mg/L | NV | <0.0050 | 0.005 | 8045259
Total Titanium (Ti) | mg/L | NV | <0.0050 | 0.005 | 8045259
Total Uranium (U) | mg/L | NV | <0.00010 | 0.0001 | 8045259
Total Vanadium (V) | mg/L | NV | <0.0050 | 0.005 | 8045259
Total Zinc (Zn) | mg/L | 3 | 0.0084 | 0.005 | 8045259 | Y
Total Zirconium (Zr) | mg/L | NV | <0.00050 | 0.0005 | 8045259
Total Calcium (Ca) | mg/L | NV | 4.7 | 0.05 | 8042183
Total Magnesium (Mg) | mg/L | NV | 0.295 | 0.05 | 8042183
Total Potassium (K) | mg/L | NV | 6.12 | 0.05 | 8042183
Total Sodium (Na) | mg/L | NV | 17.7 | 0.05 | 8042183
Total Sulphur (S) | mg/L | NV | 10.1 | 3 | 8042183
Volatiles
VPH (VHW6 to 10 - BTEX) | ug/L | NV | <300 | 300 | 8042171
Chloromethane | ug/L | NV | <1.0 | 1 | 8044829
Vinyl chloride | ug/L | NV | <0.50 | 0.5 | 8044829
Chloroethane | ug/L | NV | <1.0 | 1 | 8044829
Trichlorofluoromethane | ug/L | NV | <4.0 | 4 | 8044829
1,1-dichloroethene | ug/L | NV | <0.50 | 0.5 | 8044829
Dichloromethane | ug/L | NV | <2.0 | 2 | 8044829
trans-1,2-dichloroethene | ug/L | NV | <1.0 | 1 | 8044829
1,1-dichloroethane | ug/L | NV | <0.50 | 0.5 | 8044829
cis-1,2-dichloroethene | ug/L | NV | <1.0 | 1 | 8044829
Chloroform | ug/L | NV | 49 | 1 | 8044829
1,1,1-trichloroethane | ug/L | NV | <0.50 | 0.5 | 8044829
1,2-dichloroethane | ug/L | NV | <0.50 | 0.5 | 8044829
Carbon tetrachloride | ug/L | NV | <0.50 | 0.5 | 8044829
Benzene | ug/L | 1000 | <0.40 | 0.4 | 8044829 | Y
Methyl-tert-butylether (MTBE) | ug/L | NV | <4.0 | 4 | 8044829
1,2-dichloropropane | ug/L | NV | <0.50 | 0.5 | 8044829
cis-1,3-dichloropropene | ug/L | NV | <1.0 | 1 | 8044829
trans-1,3-dichloropropene | ug/L | NV | <1.0 | 1 | 8044829
Bromomethane | ug/L | NV | <1.0 | 1 | 8044829
1,1,2-trichloroethane | ug/L | NV | <0.50 | 0.5 | 8044829
Trichloroethene | ug/L | NV | <0.50 | 0.5 | 8044829
Chlorodibromomethane | ug/L | NV | <1.0 | 1 | 8044829
1,2-dibromoethane | ug/L | NV | <0.20 | 0.2 | 8044829
Tetrachloroethene | ug/L | 50 | <0.50 | 0.5 | 8044829 | Y
Bromodichloromethane | ug/L | NV | <1.0 | 1 | 8044829
Toluene | ug/L | 1000 | <0.40 | 0.4 | 8044829 | Y
Ethylbenzene | ug/L | 1000 | <0.40 | 0.4 | 8044829 | Y
m & p-Xylene | ug/L | NV | <0.40 | 0.4 | 8044829
Bromoform | ug/L | NV | <1.0 | 1 | 8044829
Styrene | ug/L | NV | <0.50 | 0.5 | 8044829
o-Xylene | ug/L | NV | <0.40 | 0.4 | 8044829
Xylenes (Total) | ug/L | 1000 | <0.40 | 0.4 | 8044829 | Y
1,1,1,2-tetrachloroethane | ug/L | NV | <0.50 | 0.5 | 8044829
1,1,2,2-tetrachloroethane | ug/L | NV | <0.50 | 0.5 | 8044829
1,2-dichlorobenzene | ug/L | NV | <0.50 | 0.5 | 8044829
1,3-dichlorobenzene | ug/L | NV | <0.50 | 0.5 | 8044829
1,4-dichlorobenzene | ug/L | NV | <0.50 | 0.5 | 8044829
Chlorobenzene | ug/L | NV | <0.50 | 0.5 | 8044829
VH C6-C10 | ug/L | NV | <300 | 300 | 8044829
Surrogate Recovery (%)
1,4-Difluorobenzene (sur.) | % |  | 100 |  | 8044829
4-Bromofluorobenzene (sur.) | % |  | 77 |  | 8044829
D4-1,2-Dichloroethane (sur.) | % |  | 88 |  | 8044829
Note on D9: Hun, Riley: Field condition observation
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value

## Belleville
Sampling Location, Date:
Belleville, 9/28/2015
Sample Components | Units | Bylaw | Result | RDL | QC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Calculated Parameters
Total Animal/Vegetable Oil and Grease | mg/L | 150 | 0.9 | 0.5 | 4207478 | Y
Inorganics
Total Carbonaceous BOD | mg/L | 300 | 7 | 2 | 4209218 | Y
Fluoride (F-) | mg/L | 10 | <0.10 | 0.1 | 4212137 | Y
Total Kjeldahl Nitrogen (TKN) | mg/L | 100 | 0.66 | 0.1 | 4212765 | Y
pH | pH | 6 to 10.5 | 8.19 | N/A | 4212144 | Y | #VALUE!
Phenols-4AAP | mg/L | 1 | <0.0010 | 0.001 | 4210667 | Y
Total Suspended Solids | mg/L | 350 | 15 | 10 | 4210772 | Y
Dissolved Sulphate (SO4) | mg/L | 1500 | 3.2 | 1 | 4211722 | Y
Total Cyanide (CN) | mg/L | 2 | <0.0050 | 0.005 | 4212211 | Y
Dissolved Chloride (Cl) | mg/L | 1500 | 7.9 | 1 | 4211720 | Y
Petroleum Hydrocarbons
Total Oil & Grease | mg/L | 150 | 0.9 | 0.5 | 4213097 | Y
Total Oil & Grease Mineral/Synthetic | mg/L | 15 | <0.50 | 0.5 | 4213114 | Y
ELEMENTS BY ATOMIC SPECTROSCOPY (WATER)
Metals
Total Aluminum (Al) | mg/L | 50 | 0.2 | 0.1 | 4210957 | Y
Total Antimony (Sb) | mg/L | 5 | <0.02 | 0.02 | 4210957 | Y
Total Arsenic (As) | mg/L | 1 | <0.01 | 0.01 | 4210957 | Y
Total Bismuth (Bi) | mg/L | 5 | <0.05 | 0.05 | 4210957 | Y
Total Cadmium (Cd) | mg/L | 0.7 | <0.002 | 0.002 | 4210957 | Y
Total Chromium (Cr) | mg/L | 5 | <0.01 | 0.01 | 4210957 | Y
Total Cobalt (Co) | mg/L | 5 | <0.002 | 0.002 | 4210957 | Y
Total Copper (Cu) | mg/L | 3 | <0.01 | 0.01 | 4210957 | Y
Total Iron (Fe) | mg/L | 50 | 0.61 | 0.02 | 4210957 | Y
Total Lead (Pb) | mg/L | 2 | <0.01 | 0.01 | 4210957 | Y
Total Manganese (Mn) | mg/L | 5 | 0.035 | 0.001 | 4210957 | Y
Mercury (Hg) | mg/L | 0.05 | <0.00010 | 0.0001 | 4210489 | Y
Total Molybdenum (Mo) | mg/L | 5 | <0.005 | 0.005 | 4210957 | Y
Total Nickel (Ni) | mg/L | 3 | <0.005 | 0.005 | 4210957 | Y
Total Phosphorus (P) | mg/L | 10 | 0.06 | 0.05 | 4210957 | Y
Total Selenium (Se) | mg/L | 5 | <0.02 | 0.02 | 4210957 | Y
Total Silver (Ag) | mg/L | 5 | <0.01 | 0.01 | 4210957 | Y
Total Tin (Sn) | mg/L | 5 | <0.02 | 0.02 | 4210957 | Y
Total Titanium (Ti) | mg/L | 5 | 0.015 | 0.005 | 4210957 | Y
Total Vanadium (V) | mg/L | 5 | <0.005 | 0.005 | 4210957 | Y
Total Zinc (Zn) | mg/L | 3 | 0.042 | 0.005 | 4210957 | Y
VOLATILE ORGANICS BY GC/MS (WATER)
Volatile Organics
Benzene | ug/L | 10 | <0.10 | 0.1 | 4207262 | Y
Chloroform | ug/L | 40 | <0.10 | 0.1 | 4207262 | Y
1,4-Dichlorobenzene | ug/L | 470 | <0.20 | 0.2 | 4207262 | Y
Ethylbenzene | ug/L | 160 | <0.10 | 0.1 | 4207262 | Y
Methylene Chloride(Dichloromethane) | ug/L | 210 | <0.50 | 0.5 | 4207262 | Y
1,1,2,2-Tetrachloroethane | ug/L | 40 | <0.20 | 0.2 | 4207262 | Y
Tetrachloroethylene | ug/L | 50 | <0.10 | 0.1 | 4207262 | Y
Toluene | ug/L | 270 | <0.20 | 0.2 | 4207262 | Y
Trichloroethylene | ug/L | 70 | <0.10 | 0.1 | 4207262 | Y
o-Xylene | ug/L | 520 | <0.10 | 0.1 | 4207262 | Y
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value

## London
Sampling Location,Date
London, 9/24/2015
Sample Components | Units | Bylaw | Result | RDL | QC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Calculated Parameters
Total Animal/Vegetable Oil and Grease | mg/L | 100 | 8.3 | 0.5 | 4202705 | Y
Inorganics
Total Ammonia-N | mg/L | 50 | 1.8 | 0.05 | 4208781 | Y
Total BOD | mg/L | 300 | 57 | 2 | 4204630 | Y
Fluoride (F-) | mg/L | 10 | 0.52 | 0.1 | 4205801 | Y
pH | pH | 6 to 10.5 | 8.41 | N/A | 4205792 | Y | #VALUE!
Phenols-4AAP | mg/L | 1 | 0.089 | 0.02 | 4206388 | Y
Total Suspended Solids | mg/L | 350 | 220 | 10 | 4203223 | Y
Dissolved Sulphate (SO4) | mg/L | 1500 | 40 | 1 | 4205257 | Y
Sulphide | mg/L | 2 | 0.12 | 0.02 | 4205182 | Y
Total Cyanide (CN) | mg/L | 2 | <0.0050 | 0.005 | 4205427 | Y
Dissolved Chloride (Cl) | mg/L | 1500 | 65 | 1 | 4205248 | Y
Miscellaneous Parameters
Nonylphenol Ethoxylate (Total) | mg/L | 0.2 | <0.25 | 0.25 | 4209335 | Y
Nonylphenol (Total) | mg/L | 0.02 | <0.01 | 0.01 | 4209322 | Y
Petroleum Hydrocarbons
Total Oil & Grease | mg/L | 100 | 8.3 | 0.5 | 4209625 | Y
Total Oil & Grease Mineral/Synthetic | mg/L | 15 | <0.50 | 0.5 | 4209631 | Y
ELEMENTS BY ATOMIC SPECTROSCOPY (WATER)
Metals
Total Aluminum (Al) | mg/L | 50 | 0.1 | 0.1 | 4207238 | Y
Total Arsenic (As) | mg/L | 1 | <0.01 | 0.01 | 4207238 | Y
Total Barium (Ba) | mg/L | 5 | 0.036 | 0.005 | 4207238 | Y
Total Beryllium (Be) | mg/L | 5 | <0.0005 | 0.0005 | 4207238 | Y
Total Cadmium (Cd) | mg/L | 3 | <0.002 | 0.002 | 4207238 | Y
Total Chromium (Cr) | mg/L | 5 | <0.01 | 0.01 | 4207238 | Y
Total Copper (Cu) | mg/L | 5 | 0.19 | 0.01 | 4207238 | Y
Total Iron (Fe) | mg/L | 50 | 0.39 | 0.02 | 4207238 | Y
Total Lead (Pb) | mg/L | 5 | <0.01 | 0.01 | 4207238 | Y
Total Manganese (Mn) | mg/L | 5 | 0.096 | 0.001 | 4207238 | Y
Mercury (Hg) | mg/L | 0.1 | 0.00051 | 0.0001 | 4206828 | Y
Total Molybdenum (Mo) | mg/L | 5 | <0.005 | 0.005 | 4207238 | Y
Total Nickel (Ni) | mg/L | 5 | <0.005 | 0.005 | 4207238 | Y
Total Phosphorus (P) | mg/L | 10 | 23 | 0.05 | 4207238 | N | Y
Total Selenium (Se) | mg/L | 5 | <0.02 | 0.02 | 4207238 | Y
Total Silver (Ag) | mg/L | 2 | <0.01 | 0.01 | 4207238 | Y
Total Tin (Sn) | mg/L | 5 | <0.02 | 0.02 | 4207238 | Y
Total Zinc (Zn) | mg/L | 5 | 0.32 | 0.005 | 4207238 | Y
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value

## Thorold
Sampling Location, Date:
Thorold, 9/24/2015
Sample Components | Units | Bylaw | Result | RDL | QC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Calculated Parameters
Total Animal/Vegetable Oil and Grease | mg/L | 150 | 2.7 | 0.5 | 4204544 | Y
Inorganics
Total BOD | mg/L | 300 | 540 | 2 | 4206475 | N | Y
Fluoride (F-) | mg/L | 10 | 0.11 | 0.1 | 4206727 | Y
Total Kjeldahl Nitrogen (TKN) | mg/L | 100 | 21 | 1 | 4206769 | Y
pH | pH | 6.0:11 | 7.2 | N/A | 4206728 | Y | #VALUE!
Phenols-4AAP | mg/L | 1 | 0.054 | 0.005 | 4205502 | Y
Total Suspended Solids | mg/L | 350 | 130 | 10 | 4207213 | Y
Dissolved Sulphate (SO4) | mg/L | 1500 | 34 | 1 | 4206393 | Y
Sulphide | mg/L | 1 | 0.039 | 0.02 | 4205182 | Y
Total Cyanide (CN) | mg/L | 1 | <0.0050 | 0.005 | 4205427 | Y
Petroleum Hydrocarbons
Total Oil & Grease | mg/L | NV | 2.7 | 0.5 | 4207217
Total Oil & Grease Mineral/Synthetic | mg/L | 15 | <0.50 | 0.5 | 4207218 | Y
ELEMENTS BY ATOMIC SPECTROSCOPY (WATER)
Metals
Mercury (Hg) | mg/L | 0.01 | <0.00010 | 0.0001 | 4204920 | Y
Total Antimony (Sb) | ug/L | 5000 | <0.50 | 0.5 | 4207345 | Y
Total Arsenic (As) | ug/L | 1000 | <1.0 | 1 | 4207345 | Y
Total Cadmium (Cd) | ug/L | 700 | <0.10 | 0.1 | 4207345 | Y
Total Chromium (Cr) | ug/L | 3000 | <5.0 | 5 | 4207345 | Y
Total Cobalt (Co) | ug/L | 5000 | <0.50 | 0.5 | 4207345 | Y
Total Copper (Cu) | ug/L | 3000 | 28 | 1 | 4207345 | Y
Total Lead (Pb) | ug/L | 1000 | <0.50 | 0.5 | 4207345 | Y
Total Molybdenum (Mo) | ug/L | 5000 | 1.2 | 0.5 | 4207345 | Y
Total Nickel (Ni) | ug/L | 2000 | <1.0 | 1 | 4207345 | Y
Total Phosphorus (P) | ug/L | NV | 4600 | 100 | 4207345
Total Selenium (Se) | ug/L | 1000 | <2.0 | 2 | 4207345 | Y
Total Silver (Ag) | ug/L | 5000 | <0.10 | 0.1 | 4207345 | Y
Total Tin (Sn) | ug/L | 5000 | <1.0 | 1 | 4207345 | Y
Total Zinc (Zn) | ug/L | 3000 | 10 | 5 | 4207345 | Y
VOLATILE ORGANICS BY GC/MS (WATER)
Volatile Organics
Benzene | ug/L | 10 | <2.0 | 2 | 4207783 | Y
Chloroform | ug/L | 40 | 3.8 | 2 | 4207783 | Y
1,2-Dichlorobenzene | ug/L | 50 | <4.0 | 4 | 4207783 | Y
1,4-Dichlorobenzene | ug/L | 80 | <4.0 | 4 | 4207783 | Y
Ethylbenzene | ug/L | 160 | <2.0 | 2 | 4207783 | Y
Methylene Chloride(Dichloromethane) | ug/L | 210 | <10 | 10 | 4207783 | Y
1,1,2,2-Tetrachloroethane | ug/L | 40 | <4.0 | 4 | 4207783 | Y
Tetrachloroethylene | ug/L | 50 | <2.0 | 2 | 4207783 | Y
Toluene | ug/L | 200 | <4.0 | 4 | 4207783 | Y
Trichloroethylene | ug/L | 50 | <2.0 | 2 | 4207783 | Y
p+m-Xylene | ug/L | NV | <2.0 | 2 | 4207783
o-Xylene | ug/L | 520 | <2.0 | 2 | 4207783 | Y
Total Xylenes | ug/L | NV | <2.0 | 2 | 4207783
Surrogate Recovery (%)
4-Bromofluorobenzene | % | - | 100 |  | 4207783
D4-1,2-Dichloroethane | % | - | 105 |  | 4207783
D8-Toluene | % | - | 97 |  | 4207783
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value

## Mississauga
Sampling Location, Date:
Mississauga, 9/25/2015
Sample Components | Units | Bylaw | Result | RDL | QC Batch | Compliance(Y/N)
RESULTS OF ANALYSES OF WATER
Calculated Parameters
Total Animal/Vegetable Oil and Grease | mg/L | 150 | 1.1 | 0.5 | 4204544 | Y
Inorganics
Total Carbonaceous BOD | mg/L | 300 | <2 | 2 | 4206554 | Y
Fluoride (F-) | mg/L | 10 | 0.6 | 0.1 | 4209055 | Y
Total Kjeldahl Nitrogen (TKN) | mg/L | 100 | <1.0 | 1 | 4210940 | Y
pH | pH | 5.5:10.0 | 8.13 | N/A | 4209051 | Y | #VALUE!
Phenols-4AAP | mg/L | 1 | <0.0010 | 0.001 | 4208475 | Y
Total Suspended Solids | mg/L | 350 | <10 | 10 | 4210772 | Y
Dissolved Sulphate (SO4) | mg/L | 1500 | 26 | 1 | 4209646 | Y
Total Cyanide (CN) | mg/L | 2 | <0.0050 | 0.005 | 4212211 | Y
Miscellaneous Parameters
Nonylphenol Ethoxylate (Total) | mg/L | 0.2 | <0.025 | 0.025 | 4209335 | Y
Nonylphenol (Total) | mg/L | 0.02 | <0.001 | 0.001 | 4209322 | Y
Petroleum Hydrocarbons
Total Oil & Grease | mg/L | NV | 1.1 | 0.5 | 4213097
Total Oil & Grease Mineral/Synthetic | mg/L | 15 | <0.50 | 0.5 | 4213114 | Y
ELEMENTS BY ATOMIC SPECTROSCOPY
Metals
Total Aluminum (Al) | mg/L | 50 | <0.1 | 0.1 | 4208707 | Y
Total Antimony (Sb) | mg/L | 5 | <0.02 | 0.02 | 4208707 | Y
Total Arsenic (As) | mg/L | 1 | <0.01 | 0.01 | 4208707 | Y
Total Cadmium (Cd) | mg/L | 0.7 | <0.002 | 0.002 | 4208707 | Y
Total Chromium (Cr) | mg/L | 5 | <0.01 | 0.01 | 4208707 | Y
Total Cobalt (Co) | mg/L | 5 | <0.002 | 0.002 | 4208707 | Y
Total Copper (Cu) | mg/L | 3 | 0.16 | 0.01 | 4208707 | Y
Total Lead (Pb) | mg/L | 3 | <0.01 | 0.01 | 4208707 | Y
Total Manganese (Mn) | mg/L | 5 | <0.001 | 0.001 | 4208707 | Y
Mercury (Hg) | mg/L | 0.01 | <0.00010 | 0.0001 | 4208547 | Y
Total Molybdenum (Mo) | mg/L | 5 | <0.005 | 0.005 | 4208707 | Y
Total Nickel (Ni) | mg/L | 3 | <0.005 | 0.005 | 4208707 | Y
Total Phosphorus (P) | mg/L | 10 | <0.05 | 0.05 | 4208707 | Y
Total Selenium (Se) | mg/L | 1 | <0.02 | 0.02 | 4208707 | Y
Total Silver (Ag) | mg/L | 5 | <0.01 | 0.01 | 4208707 | Y
Total Tin (Sn) | mg/L | 5 | <0.02 | 0.02 | 4208707 | Y
Total Titanium (Ti) | mg/L | 5 | <0.005 | 0.005 | 4208707 | Y
Total Zinc (Zn) | mg/L | 3 | 0.029 | 0.005 | 4208707 | Y
SEMI-VOLATILE ORGANICS BY GC-MS (WATER)
Semivolatile Organics
Bis(2-ethylhexyl)phthalate | ug/L | 12 | <2.0 | 2 | 4211725 | Y
Di-N-butyl phthalate | ug/L | 80 | <2.0 | 2 | 4211725 | Y
Surrogate Recovery (%)
2,4,6-Tribromophenol | % | - | 58 |  | 4211725
2-Fluorobiphenyl | % | - | 64 |  | 4211725
2-Fluorophenol | % | - | 14 |  | 4211725
D14-Terphenyl | % | - | 102 |  | 4211725
D5-Nitrobenzene | % | - | 63 |  | 4211725
D5-Phenol | % | - | 15 |  | 4211725
VOLATILE ORGANICS BY GC/MS (WATER)
Volatile Organics
Benzene | ug/L | 10 | <0.10 | 0.1 | 4207783 | Y
Chloroform | ug/L | 40 | 9.5 | 0.1 | 4207783 | Y
1,2-Dichlorobenzene | ug/L | 50 | <0.20 | 0.2 | 4207783 | Y
1,4-Dichlorobenzene | ug/L | 80 | <0.20 | 0.2 | 4207783 | Y
cis-1,2-Dichloroethylene | ug/L | 4000 | <0.10 | 0.1 | 4207783 | Y
trans-1,3-Dichloropropene | ug/L | 140 | <0.20 | 0.2 | 4207783 | Y
Ethylbenzene | ug/L | 160 | <0.10 | 0.1 | 4207783 | Y
Methylene Chloride(Dichloromethane) | ug/L | 2000 | 2.9 | 0.5 | 4207783 | Y
Methyl Ethyl Ketone (2-Butanone) | ug/L | 8000 | <5.0 | 5 | 4207783 | Y
Styrene | ug/L | 200 | <0.20 | 0.2 | 4207783 | Y
1,1,2,2-Tetrachloroethane | ug/L | 1400 | <0.20 | 0.2 | 4207783 | Y
Tetrachloroethylene | ug/L | 1000 | <0.10 | 0.1 | 4207783 | Y
Toluene | ug/L | 270 | <0.20 | 0.2 | 4207783 | Y
Trichloroethylene | ug/L | 400 | <0.10 | 0.1 | 4207783 | Y
p+m-Xylene | ug/L | NV | <0.10 | 0.1 | 4207783
o-Xylene | ug/L | NV | <0.10 | 0.1 | 4207783
Total Xylenes | ug/L | 1400 | <0.10 | 0.1 | 4207783 | Y
Surrogate Recovery (%)
4-Bromofluorobenzene | % | - | 97 |  | 4207783
D4-1,2-Dichloroethane | % | - | 103 |  | 4207783
D8-Toluene | % | - | 93 |  | 4207783
POLYCHLORINATED BIPHENYLS BY GC-ECD (WATER)
PCBs
Total PCB | ug/L | 1 | <0.05 | 0.05 | 4207171 | Y
Note: 2 external sanitary cover points were unable to be removed, so we sampled from the clean out drain in the lab
= Approcaching Bylaw Limit (>80% of Bylaw)
ND = Cannot be detected
RDL = Reporting Detection Limit
NV = No standard value

## Summary 2015
Sample Component | Date | Location | Bylaw (mg/L) | Permit Limit (mg/L) | Result (mg/L) | Designation | Comments | Row Labels | Count of Designation
Total BOD | 2015-09-25 | IRL | 300 | 800 | 360 | Over Limit | No action required. Within limits of waste discharge permit granted by City of Toronto. | BRL | 2
Total Kjeldahl Nitrogen (TKN) | 2015-09-25 | IRL | 100 |  | 120 | Over Limit | Need to investigate. Review all laboratory processes where nitrogen containing products/ reagents are used. Evaluate discharge practices and implement alternative products, where available, or alter discharge practices to reduce nitrogen levels. Consider permit amendments if unable to make changes. | Total BOD | 1
Total Phosphorus (P) | 2015-09-25 | IRL | 10 | 18 | 8.9 | Approaching Limit | No action required. Within limits of waste discharge permit granted by City of Toronto. | Total Suspended Solids | 1
Total BOD | 2015-09-17 | BRL | 500 |  | 415 | Approaching Limit | Continue with permit application underway. Have already initiated permit application for BRL. Has been significantly delayed (>1 year) due to changes in drawings for lab construction. City is cooperative and understanding and has not pressed for quicker action. | IRL | 3
Total Suspended Solids | 2015-09-17 | BRL | 600 |  | 511 | Approaching Limit |  | Total BOD | 1
Total Phosphorus (P) | 2015-09-24 | London | 10 |  | 23 | Over Limit | Need to investigate. Review all laboratory processes where phosphorus containing products/ reagents are used. Evaluate discharge practices and implement alternative products, where available, or discharge practices to reduce phosphorus levels. Consider permit application if unable to make changes. | Total Kjeldahl Nitrogen (TKN) | 1
Total BOD | 2015-09-24 | Thorold | 300 |  | 540 | Over Limit | Apply for permit | Total Phosphorus (P) | 1
[8 empty] | London | 1
[8 empty] | Total Phosphorus (P) | 1
[8 empty] | Thorold | 1
[8 empty] | Total BOD | 1
[8 empty] | Grand Total | 7